ÒCLIENT COMFORT SYSTEM (CCS)Ó

CONDITIONS OF CONTRACT SECTION 15915

CC 1 - GENERAL CONDITIONS

1.1 General

1.2 Standards and Guidelines

1.3 Shop Drawings

1.4 Warranty

1.5 Training

1.6 Approved Products

1.7 SAP Spare Point Capacity

CC 2 - INSTALLATION STANDARDS

2.1 General

2.2 Calibration

2.3 Electrical Work By The Controls Contractor

2.4 Electrical Work by the Electrical Contractor (DIV 16)

2.5 Conduit, Wiring and Cabling

2.6 Control Hardware

2.7 Installation of Control Devices

2.8 Installation of Actuators

CC 3 - SUBSTANTIAL PERFORMANCE TEST PROCEDURES

3.1 General

3.2 During SEVEN(7)-Day Test

3.3 Training and Demonstrations

3.4 Documentation

3.5 Project Acceptance

# CC 1 - GENERAL CONDITIONS

## 1.1	General

The Landlord shall provide the materials and labour necessary for a complete and fully operational Client Comfort System (CCS) including, but not limited to:

.1	The engineering and product documentation which defines all details of the CCS to be installed for review by the Corporation;

.2	All computerised and electronic hardware, including network communications devices, stand-alone panels (SAPs) and terminal unit controllers (TUCs);

.3	All hardware components necessary for a complete system, including field devices of all types (i.e. sensors, actuators, relays, contactors), transformers, wiring, conduit, raceways, and piping;

.4	All application programming, databases, graphics and other activities related to computer software or firmware, required to implement the generic start-up logic and the graphics screens (including dynamic data points and “hot” spots) defined in this specification.  Refer to Section 15930;

.5	A complete installation of all non-DDC and emergency controls listed in this specification;

.6	Labour and supervision for the installation, calibration, adjustments, checkouts, commissioning of all components and devices provided, and Substantial Performance requirements; and

.7	Complete documentation of the installed system, with commissioning reports and Operations and Maintenance manuals.

## 1.2	Standards and Guidelines

.1	Apply the BCBC Point Naming Convention to all points.

.2	Apply the BCBC Graphic Guidelines to all graphics.  All physical points specified in the project shall exist on at least one graphic.

.5	Openings through fire separations shall be sealed with an approved fire stopping product.

## 1.3	Shop Drawings

.1	Submit shop drawings for the project in accordance with Section 01340 of the General Conditions of the Contract for the Project.  Submit two additional copies of the shop drawings to the BCBC Project Manager for review by the Corporation.

.2	Submit product sheets on all computer components, standalone panels ( SAPs ), terminal unit controllers ( TUCs ), and field devices.  Cross out all data on the sheets not applicable to the project.

.3	Provide schematic(s) of the system architecture, including network, SAPs and TUCs.  Provide also wiring ladder diagrams and panel layouts as referenced by the Points Lists.

.4	Submit the required graphic screens for review by the Corporation 4 weeks prior to the Seven Day Test.

.5	Provide written software for Sequences of Operation which differ from the generic start-up logic included in Section 15930 prior to installation into the system.

.6	Submit calculations, on a panel-by-panel basis, confirming that the random access memory (RAM) requirements as defined in PS 3.7 Memory, are met.

.7	Provide recommended list of spare parts to be stocked on site.

.8	Provide an outline of the training program and the name and background of the person who will perform the training.

## 1.4	Warranty

Without restricting any warranty or guarantee implied or stipulated by law or elsewhere in the contract documents, the Controls Contractor will, at his own expense, rectify and make good any defect or fault that appears in the work within TWELVE (12) months from the date of the Certificate of Substantial Performance. Provide service inspections and servicing of equipment, if necessary, during the warranty year.

## 1.5	Training

Include a program, of at least 20 hours duration, for on-site operator training.  This program shall, at a minimum, cover the following:

.1	All procedures necessary for writing, editing, saving, uploading, and downloading of application software, point definition database, and any other software accessible to the user.

.2	The set-up, documentation, and editing of system displays for all systems and interfaces included in this contract.

.3	The set-up, documentation, and editing of totalizers, trend logs and trend graphing for operator selected points in each of the systems.

.4	All procedures necessary to set up and execute point monitoring, point command (e.g. auto/manual toggle and in manual, assigning a specific value), and  point response monitoring functions.

.5	Training for all of the foregoing shall be carried out from both the onsite user interface terminal and from a remote terminal by modem, using both the ContractorÕs full graphics interface software and/or text-based terminal mode software (if the latter is provided).

## 1.6	Approved Products

.1	The following products are approved for this project, subject to the system component and configuration restrictions listed for each manufacturer:

.1	Delta Controls

|  | HVAC System |  | Product Number |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 1 to 9 |  | 10 + |  |
|  |  |  | Thermal Zones in Building |  |  |  |
| 1. |  | Single Zone (reheat optional) |  | ICP015 |  | ICP015 |
| 2. |  | Central VAV(reheat optional) |  | ICP015 |  | ICP015 and IZ |
| 3. |  | Bypass VAV(reheat optional) |  | ICP015 |  | ICP015 |
| 4. |  | Multizone |  | ICP015 |  | ICP015 |
| 5. |  | Dual Fan Dual Duct |  | n/a |  | ICP015 and IZ |
| 6. |  | Air to Air Heat Pump |  | ICP015 |  | ICP015 |
| 7. |  | Water Loop Heat Pump |  | n/a |  | ICP015 and IZ |

Must include two (2) licensed copies of IGRAPHW.EXE software.

.2	Multinet

|  | HVAC System |  | Product Number |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1 to 9 | 10 + |
|  |  |  | Thermal Zones in Building |  |
| 1. |  | Single Zone (reheat optional) | MACH2 | MACH2; MNC100 |
| 2. |  | Central VAV(reheat optional) | MACH2 | MACH2; MNC100 & Mach-Air |
| 3. |  | Bypass VAV(reheat optional) | MACH2 | MACH2; MNC100 |
| 4. |  | Multizone | MACH2 | MACH2; MNC100 |
| 5. |  | Dual Fan Dual Duct | MACH2 | MACH2; MNC100 & Mach-Air |
| 6. |  | Air to Air Heat Pump | MACH2 | MACH2; MNC100 |
| 7. |  | Water Loop Heat Pump | MACH2 | MACH2; MNC100 & Mach I |

Must include two (2) licensed copies of MultiNet InControl for Windows software.

Static screen graphics generation software shall be Visio Technical

.2	Other vendors who wish to receive approval to bid shall submit complete data for review in accordance with Request for Approval process specified elsewhere in the contract documents.  For the CCS, the review procedure may include an all day interview session with the vendor, the Consultant and the Corporation, to evaluate capabilities in detail.  Such an interview will require attendance by technically knowledgeable staff from the vendor.  Allow time for this procedure when the approval request is submitted.

## 1.7	SAP Spare Point Capacity

Each SAP shall have the capability for 10% spare capacity for input points and 10% spare capacity for output points.

# CC 2 - INSTALLATION REQUIREMENTS

## 2.1	General

.1	The installation shall conform both to manufacturer's recommended procedures and all applicable codes and regulations to the approval of authorities having jurisdiction.

.2	All installations shall be performed by skilled and certified technicians and trades people.

.3	All equipment installed shall be mechanically stable and, as necessary, fixed to wall or floor.  Anti-vibration mounts to be provided, if required, for the proper isolation of the equipment.

.4	Equipment shall be installed so as to allow for easy maintenance access.  Equipment shall be installed such that it does not interfere in any way with access to adjacent equipment and personnel traffic in the surrounding space.

.5	Equipment shall be installed in locations providing adequate ambient conditions for its specified functioning, allowing for adequate ventilation and with no condensate traps.

.6	Co-operate with the construction team as a whole, to keep the job reasonably clear of waste material and rubbish at all times during progress of the work.

.7	Under the overall direction of the Landlord, coordinate activities and co-operate at all times with the principal Division 15 and 16 Contractors and other Contractors on the project concerning scheduling and installation of the work, all phases of commissioning, and access to work areas.

.8	All points associated with a single zone or an individual system shall be connected to the same SAP, and associated TUC.

## 2.2	Calibration

.1	Set control points immediately after installing controls.

.2	Set up and calibrate sensors and control loops during initial start-up of the systems and check, recalibrate and readjust as necessary during the Commissioning.

.3	Submit documentation to the Landlord’s mechanical consultant before the systems performance verification indicating the final set points of all controls, and confirmation that all control systems have been checked.  Documentation may be graphic or tabular.

## 2.3	Electrical Work By The Controls Contractor

.1	The following clauses generally indicate the extent of responsibility for electrical wiring included for the controls system.

.2	All wiring required for devices supplied under this Section of the Specifications, regardless of the voltage, shall be the responsibility of the Controls Contractor.

.3	All such work shall be performed in complete accordance with the Electrical Specifications and local Codes and may include the following:  (Refer to Section 15920 for exclusions or additions).

.1	Provision of control panels, pilot lights, selectors, relays, etc., required for the proper operation of the CCS.

.2	Conduit and wiring from the starter control or ASD circuits to the mechanical system control panels including 110 V wiring.

.3	Conduit and wiring required for the interlocking of mechanical system motor starters as required for the proper operation of the control system.

.4	Wiring from pilot devices, relays, contactors, or other control interface devices supplied under other Sections of the Mechanical Specifications and referenced in the points lists, required to complete the control system.

.5	Control wiring and interlocking required for refrigeration machines.

.6	Wiring from spare 15 amp circuit breakers in power panels for line voltage power sources where required by control system.  Circuit breakers shall be locking type.

.7	Wiring of mechanical component controls, i.e., boilers, chillers, etc.

.8	Two end switches on all dampers required for emergency controls (ULC Labelled).

.9	Power wiring and control wiring to stand alone panels and terminal unit controllers.

## 2.4	Electrical Work by the Electrical Contractor (DIV 16)

.1	Generally the Electrical Contractor shall be responsible for the electrical connections from starters to equipment motors, and the following: Refer to Section 15920 for exclusions or additions.

.1	All disconnect switches on lock-out station at motor locations where required by Code.

.2	Remote control on H.O.A. stations where they are not part of a mechanical control system panel.

.3	Power wiring to line voltage thermostats controlling force flow units and unit heaters, and wiring to float devices for sump pumps, etc.

.4	Power wiring to variable speed devices and from variable speed device to motors, where specified.

.5	Spare 15 amp emergency circuit, one on each floor for controls.

.6	Supply and installation of the properly sized overload heaters in the magnetic starters and thermal overload switches.

## 2.5	Conduit, Wiring and Cabling

.1	All work shall be installed to Division 16 Requirements.

.2	Where there is no alternative to supplying equipment which is not CSA certified, submit such equipment to Inspection Authorities for special inspection and obtain approval before delivery of equipment to site. Such equipment must be individually identified in the Contractor's proposal.

.3	Use coded conductors throughout with different coloured conductors for each phase and white wire for neutral.

.4	Low Voltage and Communications WiringÊÊ-ÊSize and type of low voltage control signal wiring shall be suitable for the service for which it will be put to use and be the responsibility of this Contractor; minimum wire size #18 AWG.

.5	Identify each wire and cable at every termination point.  Identify all conduits with ÒneatÓ colour bands at no more than 7.5 m intervals and on both sides of walls and floors.

.6	120V circuits shall be, at a minimum, of #12 AWG RW-90 copper.  For runs over 50 m in length, use #10 AWG-RW90 copper.

.7	All wiring in mechanical rooms and service rooms to be in conduit or raceway.  Provide 600 mm, B-X flexible connection to input and output devices where required for servicing or to accommodate vibration.

.8	All communication wiring between stand alone panels and the Operator Interface shall be installed in conduit.  Wiring from SAPs to TUCs does not have to be in conduit except in mechanical and electrical rooms, and where direct access is not available.

.9	All 120V interlock wiring and power supplies for panels to be installed in conduit.

.10	Provide 120V power supplies to all main DDC panels, separately circuited from all other loads.

.11	Low voltage wiring to input and output devices from SAPs and TUCs is not required to be installed in conduit except as noted.  Use plenum rated wire in areas used as return air plenums.  Provide sleeves where wires pass through walls and floors.  Support wires from structure or fixed equipment in ceiling spaces at minimum 2m intervals.

.12	Several TUCs may be supplied from one 120V power supply through a 120/24V transformer in accordance with the manufacturerÕs design.  Only TUCs connected to the same SAP may be connected to a common power supply.

## 2.6	Control Hardware

.1	Provide metal enclosures to meet NEMA specs for mounting motor control relays, wiring terminations, and components provided which require additional protection.

.2	All components shall be positioned to provide easy access for maintenance or replacement.

## 2.7	Installation of Control Devices

.1	Sensors provided under this contract shall be installed in accordance with the manufacturer's prescribed procedure.

.2	Sensors shall be rigidly mounted and mountings shall be adequate for the environment within which the sensor operates.

.3	Supply approved thermal wells of the appropriate size and type for sensing water temperatures, as required in the Points List, to the mechanical contractor for installation.

.4	All wires attached to sensors shall be air sealed in their conduits or in the wall to stop air transmitted from other areas affecting sensor readings.

.5	Install labels on the inside covers of all room sensors identifying the point name using peel and stick labels such as the Brother labelling system.

## 2.8	Installation of Actuators

.1	Where damper motors operate outdoor relief, exhaust and fresh air dampers, pretension damper drive linkage to ensure tight closure.

.2	Do not install damper motors on ductwork of less than 0.76 mm thick without first reinforcing it.

.3	Where a damper motor is installed on an insulated surface of a duct plenum, mount it on a stand-off bracket so as not to interfere with the continuity of the insulation.

.4	Locate damper motors so that they are easily accessible for testing and servicing.

.5	Damper motors shall be selected for the torque requirements of the damper.  Damper operators that are undersized for the application shall be replaced with larger operators, at no extra cost.

.6	Provide one damper motor and linkage for every 2 m2 damper section area, or as required to meet the torque requirements of the damper under design air-flow conditions (or minimum of one damper motor per damper section).  Do not use two motors linked together on one shaft, or by jackshaft.

# CC 3 - SUBSTANTIAL PERFORMANCE TEST PROCEDURES

## 3.1	General

The successful completion of a SEVEN(7)-day acceptance test as described herein is a prerequisite to granting Substantial Performance.  Before the SEVEN(7)-day acceptance test may begin, the CCS must be completely operational including the following:

.1	Every point shall be checked end to end to ensure accuracy and integrity of systems and be signed off by the Contractor and the Landlord’s mechanical consultant.

.2	Control logic shall be written in Operator Control Language (OCL) and shall successfully control the systems.

.3	Time schedules shall be built and in control of time-controlled equipment.

.4	Graphic displays shall be installed and fully operational for each graphic screen page as per the CCS Project Summary in Section 15930.

.5	Each control loop measured variable, controlled variable and set point if calculated, shall be placed on a FIFTEEN (15)- minute continuous trend for at least TWENTY-FOUR (24) hours to prove stability of loop.

.6	Each space sensor shall be placed on a THREE (3)-hour trend for One Hundred (100) samples.

.7	Runtime totalizer shall be set on all digital outputs.

.8	All features of system shall have been exercised.

.9	The operator shall have been briefed on operation of system.

.10	A trend on one panel shall be set up for a point from every other panel.  These points shall also be trended in their own panels for the same intervals.  Comparison of the two groups of trends will indicate if any communication problems are occurring during the SEVEN(7)-day test.

.11	All alarms shall be operational.

.12	Calibration of all sensors shall be complete.

## 3.2	During SEVEN(7)-Day Test

.1	The fire alarm shall be activated to ensure correct action of all fire and smoke sequences.

.2	A power failure for the building shall be simulated and system recovery monitored.

.3	The system shall be available for  the Corporation’s representative to exercise all features of the system.

.4	Load/save of panel programs shall be demonstrated.

.5	Demonstration of modem operation shall be required.  All functions of the CCS shall be accessed through the modem to prove operation.

.6	Demonstration of hardware low limits and damper interlocks shall be required.

.7	Spot checks of points end-to-end integrity will be carried out.  If several problems are identified, a complete reconfirmation of system integrity shall be carried out by the Contractor.  When reconfirmation has been completed, the SEVEN(7)-day test will be restarted.

.8	Any upset of system operational functionality greater than 2 hours during the SEVEN(7)-day test shall cause the test to be restarted.

.9	A temporary, fully functional operator interface and alarm printer shall be supplied by the Contractor for the SEVEN(7)-day test period. The printer shall be left on for the entire test.  All printouts will be kept for review at completion of the test.

.10	Results of all tests shall be documented by the Contractor and submitted to the Landlord’s mechanical consultant and to the Corporation for review.

.11	System speeds as defined in PS 3.6, PS 3.8, PS 3.9 and PS 4.2 will be tested during the SEVEN(7)-day test.

## 3.3	Training and Demonstrations

The complete training program shall be carried out (refer to Section CC 1).  It may be convenient to schedule the training during the SEVEN(7)-day test period.

## 3.4	Documentation

The following documentation shall be in place before completion of SEVEN(7)-day test and the granting of Substantial Performance:

.1	Panel layout sheets complete with point name, point address and wire identification number.  One copy attached to each respective panel door.

.2	All points tagged with point name, point address and panel number.

.3	System generated data sheets and graphics signed off by both the contractor and the consultant showing successful commissioning of each point.

.4	As-Built control drawings showing interface with existing controls.

.5	As-Built ladder wiring diagrams showing all hardware interlocks and panel input or output number.

.6	Complete Operators Manual.

.7	Apparatus and Maintenance Manual for all sensors, transducers, valves, operators, solid state relays, DDC main panels and zone controllers.

.8	Graphic plates of floor plans showing sensors, terminals, devices, zoning and stand-alone panel locations.

.9	Electrical approval certificate.

.10	All of the above information, with the exception of #2 (point tags) shall be bound and presented in TWO (2) manuals to be left on site.

.11	A copy of each graphical screen page included in Section 15930 shall be signed off and dated by the Contractor and the Landlord’s mechanical consultant.  Any changes shall be noted.  This signed set shall be left on site as the Òas-installed drawingsÓ.

In addition, a summary print-out generated by the supplied system of each group of point types for each panel shall be printed after commissioning and calibration.  Each sheet shall be signed by the ContractorÕs commissioning person, and the Landlord’s mechanical consultant.  The print-out shall be stored in a binder on site for reference by all parties.  If any changes are noted during spot checks they shall be manually written on the original print out with the date and signature of person noting changes.

## 3.5	Project Acceptance

Once the above basic requirements are met and all other features of the system are complete and acceptable, Substantial Performance shall be granted.  A deficiency list shall be prepared and holdbacks applied.  All deficiencies shall be corrected prior to Total Performance.  Warranty shall start from the date of Substantial Performance of the work.