## Sheet1
Project Number: 123 |  | Project Name: EXAMPLE BUILDING
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1.1 | Supply Fan Start/Stop | VAV1 | SF | CR1 | 1
1.2 | Supply Fan Status | VAV1 | SF_S | V |  |  |  |  | 1
1.3 | Supply Fan Program | VAV1 | SF_PG | PG |  |  |  |  | 1
1.4 | Supply Fan Trendlog | VAV1 | SF_TL | TL |  |  |  |  | 1 | SF,SF_ASD,SAT,SAP
1.5 | Supply Fan Run Hours | VAV1 | SF_TZ | TZ |  |  |  |  | 1
1.6 | Weekly Schedule | VAV1 | WS | WS |  |  |  |  | 1
1.7 | Supply Fan ASD | VAV1 | SF_ASD | DDC |  |  | 1
2.1 | Return Fan Start/Stop | VAV1 | RF | CR1 | 1
2.2 | Return Fan Program | VAV1 | RF_PG | PG |  |  |  |  | 1
2.3 | Return Fan Trendlog | VAV1 | RF_TL | TL |  |  |  |  | 1 | RF,RAT,BSP,ASD
2.5 | Return Fan ASD | VAV1 | RF_ASD | DDC |  |  | 1
3.1 | Mixed Air Damper | VAV1 | MAD | DA2 |  |  | 1
| Mixed Air Damper Controller | VAV1 | MAD_CO | CO |  |  |  |  | 1 | use SAT:SAT_SP
| Mixed Air Damper Minimum | VAV1 | MAD_MIN | V |  |  |  |  | 1
| Mixed Air Damper Ramp | VAV1 | RAMP | V |  |  |  |  | 1
3.2 | Mixed Air Program | VAV1 | MAD_PG | PG |  |  |  |  | 1
3.3 | Mixed Air Trendlog | VAV1 | MAD_TL | TL |  |  |  |  | 1 | SF_S,FRZ,MAD,MAT
| Cooling Mode | VAV1 | CLG_MODE | V |  |  |  |  | 1
4.1 | Cooling Coil Valve | VAV1 | CCV | CV3 |  |  | 1
| Cooling Coil Controller | VAV1 | CCV_CO | CO |  |  |  |  | 1 | use SAT:SAT_SP
4.2 | Cooling Coil Trendlog | VAV1 | CLG_TL | TL |  |  |  |  | 1 | CCV,SAT_SP,SAT,EC
4.3 | Cooling Coil Program | VAV1 | CCV_PG | PG |  |  |  |  | 1
| Heating Mode | VAV1 | HTG_MODE | V |  |  |  |  | 1
5.1 | Heating Coil Valve | VAV1 | HCV | CV3 |  |  | 1
| Heating Coil Controller | VAV1 | HCV_CO | CO |  |  |  |  | 1 | use SAT:SP = 12
5.2 | Heating Program | VAV1 | HTG_PG | PG |  |  |  |  | 1
5.3 | Heating Coil Valve Trendlog | VAV1 | HCV_TL | TL |  |  |  |  | 1 | HCV,SAT_SP,SAT,HCP
5.4 | Heating Coil Pump | VAV1 | HCP | CR1 | 1
5.5 | Heating Coil Pump Run Hours | VAV1 | HCP_TZ | TZ |  |  |  |  | 1
6.1 | Evaporative Cooling | VAV1 | EC | CR1 | 1
6.2 | Evaporative Cooling Program | VAV1 | EC_PG | PG |  |  |  |  | 1
6.3 | Evaporative Cooling Run Hours | VAV1 | EC_TZ | TZ |  |  |  |  | 1
7.1 | Return Air Temperature | VAV1 | RAT | DTS2 |  |  |  | 1
8.1 | Mixed Air Temperature | VAV1 | MAT | DTS1 |  |  |  | 1
9.1 | Freeze Control | VAV1 | FRZ | FRZ |  | 1
10.1 | Room Temperature Minimum | VAV1 | RT_MIN | V |  |  |  |  | 1
10.2 | Room Temperature Average | VAV1 | RT_AVG | V |  |  |  |  | 1
10.3 | Room Temperature Maximum | VAV1 | RT_MAX | V |  |  |  |  | 1
10.4 | Room Temperature Setpoint | VAV1 | RT_SP | V |  |  |  |  | 1
10.5 | Room Temperature Trendlog | VAV1 | RT_TL | TL |  |  |  |  | 1 | SAT,MIN,AVG,MAX
10.6 | Building Pressure | VAV1 | BSP | DPS |  |  |  | 1
10.7 | Building Pressure Setpoint | VAV1 | BSP_SP | V |  |  |  |  | 1
11.1 | Supply Air Temperature | VAV1 | SAT | DTS2 |  |  |  | 1
11.2 | Supply Air Temp Setpoint | VAV1 | SAT_SP | V |  |  |  |  | 1
11.3 | Supply Air Temp Program | VAV1 | SAT_PG | PG |  |  |  |  | 1
12.1 | Supply Air Pressure | VAV1 | SAP | DPS |  |  |  | 1
12.2 | Supply Air Pressure Setpoint | VAV1 | SAP_SP | V |  |  |  |  | 1
12.3 | Supply Air Pressure Program | VAV1 | SAP_PG | PG |  |  |  |  | 1
| Supply Air Pressure Controller | VAV1 | SAP_CO | CO |  |  |  |  | 1 | use SAP:SAP_SP
| Total |  |  |  | 4 | 1 | 5 | 5 | 34
EXAMPLE