## Sheet1
Project Number: |  | Project Name:
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1.1 | Supply Fan Heating Start/Stop |  | SF_HD | CR1 | 1
1.2 | Supply Fan Heating Status |  | SF_HD_S | V |  |  |  |  | 1
1.3 | Supply Fan Heating Program |  | SF_HD_PG | PG |  |  |  |  | 1
1.4 | Supply Fan Heating Trendlog |  | SF_HD_TL | TL |  |  |  |  | 1 | SF_HD,SF_HD_ASD,HDT,HDP
1.5 | Supply Fan Heating Run Hours |  | SF_HD_TZ | TZ |  |  |  |  | 1
1.6 | Weekly Schedule |  | WS | WS |  |  |  |  | 1
1.7 | Supply Fan Heating ASD |  | SF_HD_ASD | DDC |  |  | 1
2.1 | Supply Fan Cooling Start/Stop |  | SF_CD | CR1 | 1
2.2 | Supply Fan Cooling Status |  | SF_CD_S | V |  |  |  |  | 1
2.3 | Supply Fan Cooling Program |  | SF_CD_PG | PG |  |  |  |  | 1
2.4 | Supply Fan Cooling Trendlog |  | SF_CD_TL | TL |  |  |  |  | 1 | SF_CD,SF_CD_ASD,CDT,CDP
2.5 | Supply Fan Cooling Run Hours |  | SF_CD_TZ | TZ |  |  |  |  | 1
2.6 | Supply Fan Cooling ASD |  | SF_CD_ASD | DDC |  |  | 1
3.1 | Return Fan Start/Stop |  | RF | CR1 | 1
3.2 | Return Fan Program |  | RF_PG | PG |  |  |  |  | 1
3.3 | Return Fan Trendlog |  | RF_TL | TL |  |  |  |  | 1 | RF,RAT,BSP,RF_ASD
3.4 | Return Fan Run Hours |  | RF_TZ | TZ |  |  |  |  | 1
3.5 | Return Fan ASD |  | RF_ASD | DDC |  |  | 1
4.1 | Mixed Air Damper |  | MAD | DA2 |  |  | 1
| Mixed Air Damper Controller |  | MAD_CO | CO |  |  |  |  | 1 | use:CDT:CDT_SP
| Mixed Air Damper Ramp |  | RAMP | V |  |  |  |  | 1
4.2 | Mixed Air Program |  | MAD_PG | PG |  |  |  |  | 1
4.3 | Mixed Air Trendlog |  | MAD_TL | TL |  |  |  |  | 1 | SF_CD,FRZ,MAD,MAT
5.1 | Exhaust Air Damper |  | EAD | DA2 |  |  | 1
| Exhaust Air Damper Controller |  | EAD_CO | CO |  |  |  |  | 1 | use EAP:EAP_SP
5.2 | Exhaust Air Pressure |  | EAP | DPS |  |  |  | 1
5.3 | Exhaust Air Pressure Setpoint |  | EAP_SP | V |  |  |  |  | 1
5.4 | Exhaust Air Damper Program |  | EAP_PG | PG |  |  |  |  | 1
5.5 | Exhaust Air Damper Trendlog |  | EAD_TL | TL |  |  |  |  | 1 | EAD,EAP,BSP,EAP_SP
6.1 | Gas Valve |  | GV | DDC |  |  | 1
| Gas Valve Controller |  | GV_CO | CO |  |  |  |  | 1 | use HDT:HDT_SP
6.2 | Heating Program |  | HD_PG | PG |  |  |  |  | 1
6.3 | Gas Valve Trendlog |  | GV_TL | TL |  |  |  |  | 1 | GV,HDT,HDT_SP
| Cooling Mode |  | CLG_MODE | V |  |  |  |  | 1
7.1 | Stage 1-DX |  | DX1 | CV3 |  |  | 1
7.2 | DX1 Run Hours |  | DX1_TZ | TZ |  |  |  |  | 1
7.3 | DX Program |  | CLG_PG | PG |  |  |  |  | 1
__.1 | Stage -DX |  | DX____ | CV3 | [5 empty] | As Required
__.2 | DX Run Hours |  | DX _TZ | TZ | [5 empty] | As Required
8.1 | Evaporative Cooling |  | EC | CR1 | 1
8.2 | Evaporative Cooling Program |  | EC_PG | PG |  |  |  |  | 1
8.3 | Evaporative Cooling Run Hours |  | EC_TZ | TZ |  |  |  |  | 1
9.1 | Return Air Temperature |  | RAT | DTS2 |  |  |  | 1
10.1 | Mixed Air Temperature |  | MAT | DTS1 |  |  |  | 1
11.1 | Freeze Control |  | FRZ | FRZ |  | 1
12.1 | Room Temperature Minimum |  | RT_MIN | V |  |  |  |  | 1
12.2 | Room Temperature Average |  | RT_AVG | V |  |  |  |  | 1
12.3 | Room Temperature Maximum |  | RT_MAX | V |  |  |  |  | 1
12.4 | Room Temperature Setpoint |  | RT_SP | V |  |  |  |  | 1
12.5 | Room Temperature Trendlog |  | RT_TL | TL |  |  |  |  | 1 | MIN,AVG,MAX
12.6 | Building Pressure |  | BSP | DPS |  |  |  | 1
12.7 | Building Pressure Setpoint |  | BSP_SP | V |  |  |  |  | 1
13.1 | Supply Air Hot Deck Temp |  | HDT | DTS2 |  |  |  | 1
13.2 | Supply Air HD Temp Setpoint |  | HDT_SP | V |  |  |  |  | 1
13.2 | Supply Air HD Temp Program |  | HDT_PG | PG |  |  |  |  | 1
14.1 | Supply Air HD Pressure |  | HDP | DPS |  |  |  | 1
14.2 | Supply Air HD Pres Setpoint |  | HDP_SP | V |  |  |  |  | 1
14.3 | Supply Air HD Pres Program |  | HDP_PG | PG |  |  |  |  | 1
| Supply Air HD Pres Controller |  | HDP_CO | CO |  |  |  |  | 1 | use HDP:HDP_SP
15.1 | Supply Air Cold Deck Temp |  | CDT | DTS2 |  |  |  | 1
15.2 | Supply Air CD Temp Setpoint |  | CDT_SP | V |  |  |  |  | 1
15.3 | Supply Air CD Temp Program |  | CDT_PG | PG |  |  |  |  | 1
16.1 | Supply Air CD Pressure |  | CDP | DPS |  |  |  | 1
16.2 | Supply Air CD Pres Setpoint |  | CDP_SP | V |  |  |  |  | 1
16.3 | Supply Air CD Pres Program |  | CDP_PG | PG |  |  |  |  | 1
| Supply Air CD Pres Controller |  | CDP_CO | CO |  |  |  |  | 1 | use CDP:CDP_SP
| Total |  |  |  | 4 | 1 | 7 | 8 | 44