## Sheet1
Project Number: |  | Project Name:
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1.1 | Supply Fan Start/Stop |  | SF | CR1 | 1
1.2 | Supply Fan Amps |  | SF_AMP | CS1 |  |  |  | 1
| Supply Fan Status |  | SF_S | V |  |  |  |  | 1
1.3 | Supply Fan Program |  | SF_PG | PG |  |  |  |  | 1
1.4 | Supply Fan Trendlog |  | SF_TL | TL |  |  |  |  | 1 | SF,SF_AMP,SAT,SAT_SP
1.5 | Supply Fan Run Hours |  | SF_TZ | TZ |  |  |  |  | 1
1.6 | Weekly Schedule |  | WS | WS |  |  |  |  | 1
3.1 | Mixed Air Damper |  | MAD | DA2 |  |  | 1
| Mixed Air Damper Controller |  | MAD_CO | CO |  |  |  |  | 1 | use SAT:SAT_SP
| Mixed Air Damper Minimum |  | MAD_MIN | V |  |  |  |  | 1
| Mixed Air Damper Ramp |  | RAMP | V |  |  |  |  | 1
3.2 | Mixed Air Program |  | MAD_PG | PG |  |  |  |  | 1
3.3 | Mixed Air Trendlog |  | MAD_TL | TL |  |  |  |  | 1 | SF_S,FRZ,MAD,MAT
| Cooling Mode |  | CLG_MODE | V |  |  |  |  | 1
4.1 | Stage 1-DX |  | DX1 | CR1 | 1
4.2 | DX1 Run Hours |  | DX1_TZ | TZ |  |  |  |  | 1
4.3 | DX Program |  | CLG_PG | PG |  |  |  |  | 1
__.1 | Stage -DX |  | DX__ | CR1 | [5 empty] | As Required
__.2 | DX Run Hours |  | DX _TZ | TZ | [5 empty] | As Required
| Heating Mode |  | HTG_MODE | V |  |  |  |  | 1
5.1 | Heating Coil Valve |  | HCV | CV3 |  |  | 1
| Heating Coil Controller |  | HCV_CO | CO |  |  |  |  | 1 | use SAT:SAT_SP
5.2 | Heating Program |  | HTG_PG | PG |  |  |  |  | 1
5.3 | Heating Coil Valve Trendlog |  | HCV_TL | TL |  |  |  |  | 1 | HCV,SAT_SP,SAT,HCP
5.4 | Heating Coil Pump |  | HCP | CR1 | 1
5.5 | Heating Coil Pump Run Hours |  | HCP_TZ | TZ |  |  |  |  | 1
7.1 | Return Air Temperature |  | RAT | DTS2 |  |  |  | 1
8.1 | Mixed Air Temperature |  | MAT | DTS1 |  |  |  | 1
9.1 | Freeze Status |  | FRZ | FRZ |  | 1
10.1 | Room Temperature Minimum |  | RT_MIN | V |  |  |  |  | 1
10.2 | Room Temperature Average |  | RT_AVG | V |  |  |  |  | 1
10.3 | Room Temperature Maximum |  | RT_MAX | V |  |  |  |  | 1
10.4 | Room Temperature Setpoint |  | RT_SP | V |  |  |  |  | 1
10.5 | Room Temperature Trendlog |  | RT_TL | TL |  |  |  |  | 1 | SAT,MIN,AVG,MAX
11.1 | Supply Air Temperature |  | SAT | DTS2 |  |  |  | 1
11.2 | Supply Air Temp Setpoint |  | SAT_SP | V |  |  |  |  | 1
11.3 | Supply Air Temp Program |  | SAT_PG | PG |  |  |  |  | 1
| Total |  |  |  | 3 | 1 | 2 | 4 | 25