## Sheet1
Project Number: |  | Project Name:
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1 | Room Temperature |  | HPxyz_RT | RTS1 |  |  |  | 1
2 | Room Temperature Setpoint |  | HPxyz_RT_SP | V |  |  |  |  | 1
3 | Room Trendlog |  | HPxyz_RT_TL | TL |  |  |  |  | 1 | RT,SAT,REV,C
| Room Override Button |  | HPxyz_OR_B | RTS1 |  | 1 |  |  |  | Same sensor as 1
4 | Room Override Time Left |  | HPxyz_OR | V |  |  |  |  | 1
5 | Room Weekly Schedule |  | HPxyz_WS | WS | [5 empty] | See Spec 15925
6 | Reversing Valve |  | HPxyz_REV | CR1 | 1
7 | Compressor Control |  | HPxyz_C | CR1 | 1
8 | Heat Pump Program |  | HPxyz_PG | PG |  |  |  |  | 1
9 | Supply Air Temperature |  | HPxyz_SAT | DTS1 |  |  |  | 1
10 | Supply Fan |  | HPxyz_F | CR1 | 1
| Total |  |  |  | 3 | 1 | 0 | 2 | 4
NOTE: x = Floor #
yz = Heat Pump # of Floor #
For Heat Pump # see mechanical schedule