Guideline Contents

1.	Introduction and General Concepts

2.	Graphic Concepts

.1	Graphic Overview of Inter-relationships

.2	Main Menu Graphic - A

.3	Index Graphic - A1

.3	Floor Graphic - B

.4	Details Floor Graphic B1

.4	AHU Graphic - C

.5	CCS Graphic - D

.6	Help Graphic - E

3.	Concepts To Speed Graphic Generation

.1	File Conversion (Auto Cad, TIF, GIF, etc)

.2	Screen Capture

.3	Scanning

.4	Transparency Tracing

.5	Tricks and Traps

4.	Glossary of Computer Industry Existing Graphic Standards

1.	Introduction

These graphic guidelines have been developed to provide standardization in concepts and quality for the computerized color graphics that are part of the Client Comfort Systems.

This document should in no way impede your creative side to generate custom graphics for each project.  Its purpose is to provide guidelines as to the minimum requirements of your graphic set and to standardize graphic controlled hot spots and how we move through the graphic set.

The general concepts graphically presented in Section 2 provide the basis of the guidelines.  Please forward your perceptions and comments on any aspect of the guideline so that we may consider inclusion in future updates.  Please fax all your comments to Director, Energy and Environment 387-1878.

General Concepts

The following overview shows the inter-relationship of mandatory graphics.  The guideline is intended to provide conventions for movement and symbolism for graphics.  Since the graphic set will be operated in the Windows environment use of left upper corner should be left blank for access to pull down menus.  Vendor operating systems also use this area.  The right corner should be left blank as several systems use this area to display the time.  Avoid putting any information or active icons close to the edge of the screen as this may cause problems when sizing windows and or problems with screen setup with various monitors.  Determine where vendors display their alarm lines and avoid conflict.  Most alarm lines overwrite existing graphics so display is not a major concern, but active icons are if they appear under the alarm line.

Mandatory Requirements

Graphic Title  - The graphic title will be located at the top of each screen.

Date  - Each graphic will be dated with the last update.

Key Plan  -  A key plan will be provided in the lower right hand corner with each graphic screen showing the related floor area plus the number of floors or levels.  The shaded area will depict the area served by this graphic.  Clicking on the level or floor number will present the corresponding location on that floor graphic.  Clicking on the non-shaded areas will present the graphic representing that area on the same floor.

Menu Bar - The menu bar will be located at the bottom of each screen, not to interfere with the alarming line.  The bar must be placed exactly in the same location on each screen to allow browsing through the system by clicking on the buttons without moving the mouse.

MAIN MENU	The return to the Main Menu must always be in the furthest left 				location of the bar on all graphics.

PREVIOUS	The Previous graphic button must be second from the left on all 				graphics.

Special Custom button(s)  Commands particular to the graphic screen.

COMMAND	The Command mode button must be third from the right on main 				menu only.

BYE		Sign off will always be the second from the far right on main menu 				and index.

HELP		Help will always be on the far right of the menu bar on all graphics.

The above is to standardize movement throughout the graphic set.

Point Convention

The actual point will be located as close as possible to the graphical representation of actual location.  If the point has an associated setpoint this point will be located directly below the actual point and be in a different colour.

ON OFF Status Convention

Status point of equipment will be defined as ON or OFF and located on top of command points.

Command Points

Command points should be defined as Start/Stop or Enable/Disable, etc, but not as ON/OFF.

Weekly Schedules

Weekly schedules will be symbolized by a clock icon.  Access will be from every time controlled system plus the Index.  The Index will take you to a screen of all time schedules whereas time controlled points on a particular system graphic will take you only to the controlling schedule.

Trend Data/Graphs

Trend graphs will be symbolized by a box with a graph line icon.  Icon will be placed near the actual analog point that will be trended.  On floor graphic, the sensor symbol will become an icon to access trend data for that zone.

OCL Programs

Will be symbolized by a box with a horizontal lines icon and will be accessed from every output.  This concept will tie in with the Corporation's concept of output oriented code.

Runtime Hours

Runtime hours will be symbolized by 999 HR in a box.  This icon will be placed as close as possible to the actual point being totalized.  The actual total hours will replace the 999 HR on the screen.  Clicking on the icon will provide more information.

Text Size

Text size should be large enough to be easily read.  If you must reduce text size to get all information in you need a further zoom graphic.  Use a pleasing color contrast between lettering and background.

Use Of Colour

-  Avoid using too much color.  Without planning you could over use color and actually detract from the visual impact, as well as causing eye strain.

-  Attempt to match the visual impact of color with the importance of the information.

Eg:	- bright red or yellow for alarm information;

- next brightest color for dynamic information such as temperature and status;

- next brightest color for action items such as icons;

- darker color for passive, but important information such as schematic lines;

- pastel color for passive, less important information such as backgrounds.

- Attempt to maintain color consistency, ie all air systems similar, all hot water lines the same color, all chilled water lines the same.

The examples in these guidelines show one way of interpreting the use of color following these suggestions.

2.	Graphic Concepts

.1	Graphic Overview of Inter-relationships

.2	Main Menu Graphic - A

.3	Index Graphic - A1

.3	Floor Graphic - B

.4	Details Floor Graphic B1

.4	AHU Graphic - C

.5	CCS Graphic - D

.6	Help Graphic - E

3.	Concepts to Speed Graphic Generation

.1 	File Conversion

Several complexes have computerized the space management floor plates on an AutoCad system.  Most AutoCad system information can be transferred electronically to most file formats.  In most cases too much information is stored on AutoCad for good video screen presentation graphics.  It is normally necessary to sit with a CAD operator and get only the simplest floor plate information on the screen and remove all layers before output to .DXF files.  Text information usually causes problems as the fonts are different in most manufacturers' graphic systems.  It is often easier to add text later in the font you wish.  Major clean up is usually required with most file conversions.

.2	Screen Capture

If file conversion is not an option, screen capture should be considered if system supports bit map type graphics.  Resolution of graphics are limited by overall screen resolution.  Problems are often caused later if graphics need to be edited.  Original graphics programs must be used requiring two sets of graphic records.  Screen capture does not allow re-sizing once screen is captured.  Usually not applicable to vector type graphics except if third party conversion programs are used.  This is a workable but painful method.

.3	Scanning

If the information required to be turned into graphics is not available in electronic media, paper media can be scanned and digitized into computer files.  Most scanners support many file types.  These files can then be converted using file conversion routines into the required format.  Low cost hand scanners can be used for low volumes of work but bed type scanners are preferred for large volumes plus the need to auto stitch scanned strips is eliminated.

.4	Transparency Tracing

When a scanner is not available or drawings have more data than required, transparency tracing offers a manual method of quickly tracing only the information you require off a drawing.  First photocopy the drawing to be traced on to a clear transparency like the ones used for overheads.  Then tape the transparency to your screen and trace under the transparency using the preferred drawing package.  This method works amazingly well allowing for quick transfer of the pertinent data.  If you have access to a reducing/expanding copier you can usually size drawing before copying to a transparency.

.5	Tricks and Traps

.1	Screen presentation graphics are quite different than graphics on paper media.  The screen resolution and speed at which data is presented requires that print be larger, drawings simpler, colors softer and dynamic information as large as possible.

.2	Your colour choices should be reviewed on a black and white screen as most laptops do not support color.

.3	Most manufacturers keep drawings in a library or directory.  Be sure you understand the inter-relationship of how the system calls the graphics.  It is often not just as easy as moving or renaming graphics because of the interlinking created on each graphic.

.4	Store icons that you will use over and over as objects so that they may be sized and added to typical drawings.

.5	Use typical drawings and add or delete custom information for minimum effort and maximum graphic generation speed.  Think about how you might use portions of a graphic again and save it in several pieces, each under a separate file name.

.6	Standardize as much as possible.  It is often easier to modify a complete operating library file from another building than to begin again.

It is hoped that these guidelines will do much to aid standardization, reduce required effort and increase speed to build comprehensive graphics.

4.	Glossary of Computer Industry Existing Graphic Standards

File formats are standardized methods of organizing images based on image class and compression type.  Common file types include the following:

-	TIFF (extension .TIF) - Tagged Information File Format; usable by most Window applications, common printing standards.

-	GIF (extension .GIF) - Graphics Interchange Format, developed by CompuServe Incorporated.

-	PCX (extension .PCX) - developed by ZSoft Corporation.

-	BMP (extension .BMP) - an internal format used by Windows and OS/2.

-	CUT (extension .CUT) - a file format developed by Media Cybernetics; it is the main file format of the popular Dr HALO IV paint package.

-	IMG (extension .IMG) - developed by Digital Research, and used extensively by Ventura Publisher.

-	MSP (extension .MSP) - developed by Microsoft for Microsoft Paint.

-	TGA (extension .TGA) - TARGA - developed by True Vision.

-	DXF (extension .DXF) - output file of AUTOCAD, importable in most high end graphic packages.

Some CCS vendors use custom file formats, but most provide a method of conversion from these standard file formats or offer screen capture methods.  Vendors who are completely Window compatible are able to deal with the above formats and those that are not are presently implementing the necessary changes.